## Main Lab
| Zone | DEPT | Rm | FH No. | BRAND | SIZE(MM) | VS FAN | Type | CAV (Y/N) | VAV (Y/N) | AutoSash | Normal Flow (Y/N) | Low Flow (Y/N) | Extra-Low Flow (Y/N) | Acceptable Range of Face Velocity | min flow (L/S) | Maximum Sash Hieght of Fume Hoods with a Minimum Flow Rate | Max flow rate | Occupancy Data in BMS (Y-1/N) | Calibration Check (Y/N) | Notes
1 | K | ECE | 1043 | FH167 | MORGAN & GRUNDY | 1200 | EF-ENT-140-4 | BBQ | Y | N |  | N | N | N | N/A | N/A | N/A | N/A
2 | K | ECE | 1047A | FH161 | MORGAN & GRUNDY | 1500 | EF-ENT-140-4 | BBQ | Y | N |  | N | N | N | N/A | N/A | N/A | N/A
3 | K | ECE | 1047A | FH162 | MORGAN & GRUNDY | 1500 | EF-ENT-140-4 | BBQ | Y | N |  | N | N | N | N/A | N/A | N/A | N/A
4 | K | ECE | 1047A | FH163 | MORGAN & GRUNDY | 1500 | EF-ENT-140-4 | BBQ | Y | N |  | N | N | N | N/A | N/A | N/A | N/A
5 | K | ECE | 1047A | FH170 | MORGAN & GRUNDY | 1200 | EF-ENT-140-4 | BBQ | Y | N |  | N | N | N | N/A | N/A | N/A | N/A
6 | J | CIVL | 1207C | FH291 | RENGGLI | 1500 | EF-J-152-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 200.75
7 | J | CIVL | 1209C | FH294 | WALDNER | 1500 | EF-J-152-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 238.7
8 | J | CIVL | 1211 | FH226 | LAB FURNISHING | 1500 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
9 | J | MAE | 1213 | FH265 | KEWAUNE | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 227.7
10 | J | CLS | 1215 | FH119 | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
11 | K | CHEM | 2123 | FC041 | LAB FURNISHING | 1500 | EF-K-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
12 | L | MCPF | 2151 | FH178 | MORGAN & GRUNDY | 1500 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
13 | L | CAMP | 2162A | FH324 | MOTT | 1500 | EF-L3-157-107/108 | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319.275
14 | L | ECE | 2164 | FH475 | CLEAN AIR | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
15 | L | ECE | 2166 | FC042 | LAB FURNISHING | 1500 | EF-L3-157-107/108 | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
16 | L | ECE | 2166 | FC054 | LAB FURNISHING | 1200 | EF-L3-157-107/108 | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
17 | H | ECE | 2227 | FC031 | LAB FURNISHING | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
18 | H | CHEM | 2228 | FH710 | CHEMFAST | 1200 |  | DUCTLESS |  |  |  | Y | N | N | 0.35M/S at 200mm sash height | N/A | N/A | N/A
19 | H | CHEM/LIFS | 2229 | FC053 | LAB FURNISHING | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
20 | H | LIFS | 2230K | FH290 | WALDNER | 1200 | EF-H-152-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5
21 | H | PHYS | 2232 | FC002 | LAB FURNISHING | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
22 | H | ECE | 2234 | FH253 | MOTT | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319.275
23 | H | PHYS | 2237 | FH724 | WALDNER | 1500 | EF-H-152-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5
24 | K | HSEO | 3107 | FC030 | WALDNER | 1500 | EF-K-157-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 238.7 | 1 | N (Wait for Budget)
25 | K | HSEO | 3107D | FC003 | LAB FURNISHING | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220.275 | 1 | Y
26 | K | HSEO | 3107 | FC029 | WALDNER | 1500 | EF-K-157-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 238.7 | 1 | N (Wait for Budget)
27 | L | ECE | 3112 | FC004 | LAB FURNISHING | 1200 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220.275 | 1 | Y
28 | L | ECE | 3112 | FC040 | LAB FURNISHING | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
29 | L | ECE | 3125B | FH245 | ESCO | 1200 |  | DUCTLESS |  |  |  | Y | N | N | 0.35M/S at 200mm sash height | N/A | N/A | N/A
30 | J | CIVL | 3201 | FH705 | WALDNER | 1500 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
31 | J | CIVL | 3201 | FH706 | WALDNER | 1500 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
32 | J | CIVL | 3201 | FH707 | RENGGLI | 1500 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 200.75
33 | J | CIVL | 3202 | FH704 | WALDNER | 1500 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
34 | J | CIVL | 3212 | FH271 | WALDNER | 1500 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
35 | H | NFF | 3231 | FC009 | LAB FURNISHING | 1200 | EF-H-152-105A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
36 | K | ENVR | 4094 | FH488 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
37 | K | ENVR | 4094 | FH494 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
38 | K | ENVR | 4094 | FH517 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
39 | K | ENVR | 4094 | FH520 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
40 | K | ENVR | 4096 | FH076 | WALDNER | 1500 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5
41 | K | ENVR | 4105 | FH491 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
42 | K | ENVF | 4109C | FH067 | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5
43 | K | ENVF | 4109C | FH069 | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5
44 | K | ENVR | 4110 | FH527 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
45 | K | ENVR | 4111 | FH495 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
46 | K | ENVR | 4113 | FH301 | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
47 | K | ENVR | 4114 | FH251 | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
48 | L | PHYS | 4115 | FH277 | WALDNER | 1200 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5 | 1 | N (Wait for Budget)
49 | L | PHYS | 4115A | FH278 | WALDNER | 1200 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5 | 1 | N (Wait for Budget)
50 | L | PHYS | 4115D | FH281 | RENGGLI | 1200 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5
51 | L | PHYS | 4116A | FH279 | WALDNER | 1200 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5 | 1 | N (Wait for Budget)
52 | L | PHYS | 4116B | FH282 | RENGGLI | 1200 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5
53 | L | PHYS | 4117 | FH280 | WALDNER | 1200 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5 | 1 | N (Wait for Budget)
54 | L | PHYS | 4118 | FH005 | MORGAN & GRUNDY | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
55 | L | PHYS | 4119B | FH181 | LAB FURNISHING | 1200 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220.275 | 1 | Y
56 | L | PHYS | 4121B | FH006 | MORGAN & GRUNDY | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
57 | L | PHYS | 4123 | FH007 | MORGAN & GRUNDY | 1200 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220.275 | 1 | Y
58 | L | PHYS | 4125 | FH286 | RENGGLI | 1200 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5
59 | L | PHYS | 4125 | FH287 | RENGGLI | 1200 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5
60 | L | PHYS | 4126 | FH008 | MORGAN & GRUNDY | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
61 | L | PHYS | 4139 | FH010 | LAB FURNISHING | 1200 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220.275 | 1 | Y
62 | L | PHYS | 4141 | FH011 | MORGAN & GRUNDY | 1200 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220.275 | 1 | Y
63 | L | PHYS | 4142 | FH292 | RENGGLI | 1500 | EF-L-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 200.75
64 | L | PHYS | 4145 | FH206 | NUAIRE | 1800 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 264 | 1 | Y
65 | L | PHYS | 4145 | FH231 | APMG | 1200 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 235.125 | 1 | Y
66 | L | BRI | 4150 | FH273 | WALDNER | 1500 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
67 | L | BRI | 4150 | FH274 | WALDNER | 1500 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
68 | L3 | LIFS | 4160 | FH332 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
69 | L3 | LIFS | 4160 | FH333 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
70 | L3 | LIFS | 4160B | FH331 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
71 | J | LIFS | 4218 | FH283 | CHEMFAST | 1500 |  | DUCTLESS |  |  |  | Y | N | N | 0.35M/S at 200mm sash height | N/A | N/A | N/A
72 | H | MAE | 4222 | FH254 | MOTT | 1500 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319.275
73 | H | MAE | 4222B | FH266 | WALDNER | 1500 | EF-H-152-06 | BBQ | Y | N | Y | N | N | N | N/A | N/A | N/A | N/A
74 | H | MAE | 4225 | FH476 | CLEAN AIR | 1500 | EF-H-152-102A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
75 | H | MAE | 4225 | FH493 | CLEAN AIR | 1500 | EF-H-152-102A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
76 | H | MAE | 4225 | FH243 | KEWAUNE | 1500 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 326.7
77 | H | MAE | 4225 | FH252 | MOTT | 1500 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319.275
78 | H | MAE | 4227 | FH330 | MOTT | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319.275
79 | H | AEMF | 4228 | FH055 | KEWAUNE | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 326.7
80 | H | AEMF | 4229 | FC026 | LAB FURNISHING | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
81 | H | AEMF | 4229 | FC049 | LAB FURNISHING | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
82 | H | AEMF | 4229 | FH169 | MORGAN & GRUNDY | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
83 | H | AEMF | 4229 | FH075 | MORGAN & GRUNDY | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
84 | K | EVNG | 6102 | FC018 | LAB FURNISHING | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220.275 | 1 | Y
85 | K | FMO/DMSF | 6103 | FC017 | LAB FURNISHING | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220.275 | 1 | Y
86 | K | CBE | 6104 | FH230 | APMG | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 235.125 | 1 | Y
87 | K | MAE | 6105 | FC019 | LAB FURNISHING | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220.275 | 1 | Y
88 | K | MAE | 6105 | FC020 | LAB FURNISHING | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220.275 | 1 | Y
89 | K | CLS | 6109 | FH318 | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275
90 | K | CBE | 6113 | FH051 | KOTTERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5 | 1 | Y
91 | K | CBE | 6114 | FH084 | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5 | 1 | Y
92 | K | CBE | 6114 | FH025 | KOTTERMAN | 1800 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325.325
93 | K | CBE | 6115 | FH269 | WALDNER | 1500 | EF-K-157-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 238.7 | 1 | N (Wait for Budget)
94 | K | CBE | 6115 | FH270 | WALDNER | 1500 | EF-K-157-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 238.7 | 1 | N (Wait for Budget)
95 | L | CBE | 6117 | FH285 | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
96 | L | CBE | 6118 | FH059 | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5 | 1 | Y
97 | L | CBE | 6119 | FH078 | KOTTRERMAN | 1500 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5 | 1 | Y
98 | L | CHEM | 6120 | FH017 | LAB FURNISHING | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
99 | L | CHEM | 6120 | FC032 | LAB FURNISHING | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
100 | L | CBE | 6121 | FH061 | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5 | 1 | Y
101 | L | CHEM | 6122 | FH018 | LAB FURNISHING | 1800 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 373.725 | 1 | Y
102 | L | CHEM | 6122 | FH020 | KOTTRERMAN | 1500 | EF-L-157-102A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5 | 1 | Y
103 | L | CHEM | 6122 | FH021 | KOTTRERMAN | 1500 | EF-L-157-102A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5 | 1 | Y
104 | L | CHEM | 6122 | FH041 | KOTTRERMAN | 1800 | EF-L-157-102A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325.325 | 1 | Y
105 | L | CHEM | 6124B | FH026 | WALDNER | 1800 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 81 | 100mm | 211.75
106 | L | CHEM | 6124B | FH288 | RENGGLI | 1200 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5
107 | L | CHEM | 6124B | FH289 | RENGGLI | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 200.75
108 | L | CHEM | 6124B | FH039 | WALDNER | 1800 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 81 | 100mm | 211.75
109 | L | CHEM | 6125 | FH022 | KOTTERMAN | 1800 | EF-L-157-102A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325.325 | 1 | Y
110 | L | CHEM | 6125 | FH024 | KOTTERMAN | 1800 | EF-L-157-102A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325.325 | 1 | Y
111 | L | CHEM | 6125 | FH040 | KOTTERMAN | 1800 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325.325
112 | L | CHEM | 6125 | FH700 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
113 | L | CHEM | 6125 | FH701 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
114 | L | CHEM | 6125 | FH702 | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
115 | L | CHEM | 6125 | FH703 | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
116 | L | BCRF | 6127 | FH209 | CMS | 1200 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 245.025 | 1 | Y
117 | L | PHYS | 6138 | FH028 | MORGAN & GRUNDY | 1200 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220.275 | 1 | Y
118 | L | BRI | 6141 | FH191 | MOTT | 1800 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 396 | 1 | Y
119 | L3 | CHEM | 6143 | FH321 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
120 | L3 | CHEM | 6143 | FH322 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
121 | L3 | CCM | 6145 | FH319 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
122 | L3 | CCM | 6145 | FH320 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
123 | L3 | BCRF | 6146 | FH325 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
124 | L3 | R&D | 6147 | FH317 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
125 | L3 | FINTEX | 6148 | FH327 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
126 | L3 | FINTEX | 6148 | FH328 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
127 | L3 | NAMI | 6149 | FH708 | RENGGLI | 1200 | EF-L3-157-107/108 | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5 | 1 | Y
128 | L3 | NAMI | 6149 | FH709 | RENGGLI | 1200 | EF-L3-157-107/108 | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5 | 1 | Y
129 | L3 | NAMI | 6150 | FH323 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
130 | J | LIFS | 6201 | FH711 | WALDNER | 1200 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5 | 1 | N (Wait for Budget)
131 | J | LIFS | 6201 | FH712 | WALDNER | 1200 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5 | 1 | N (Wait for Budget)
132 | J | LIFS | 6201 | FH713 | WALDNER | 1200 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5 | 1 | N (Wait for Budget)
133 | J | LIFS | 6201 | FH714 | WALDNER | 1200 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5 | 1 | N (Wait for Budget)
134 | J | LIFS | 6219 | FH145 | MORGAN & GRUNDY | 1200 | EF-J-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
135 | J | LIFS | 6220 | FH144 | MORGAN & GRUNDY | 1200 | EF-J-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
136 | J | LIFS | 6221 | FH166 | MORGAN & GRUNDY | 1200 | EF-J-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
137 | J | LIFS | 6223 | FH143 | MORGAN & GRUNDY | 1200 | EF-J-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
138 | J | LIFS | 6224 | FH142 | MORGAN & GRUNDY | 1200 | EF-J-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
139 | J | LIFS | 6225 | FH138 | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
140 | J | LIFS | 6231 | FH140 | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
141 | J | LIFS | 6233A | FC010 | LAB FURNISHING | 1500 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
142 | J | LIFS | 6233B | FH137 | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
143 | J | LIFS | 6237 | FH135 | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
144 | J | LIFS | 6243 | FH136 | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
145 | J | LIFS | 6244 | FH132 | LAB FURNISHING | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
146 | J | LIFS | 6246 | FH130 | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
147 | J | LIFS | 6248 | FH129 | LAB FURNISHING | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
148 | J | LIFS | 6255 | FH267 | MOTT | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 245.025
149 | J | LIFS | 6256A | FC056 | LAB FURNISHING | 1200 |  | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
150 | J | LIFS | 6260 | FH312 | MOTT | 1500 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319.275
151 | H | LIFS | 6274 | FH099 | LAB FURNISHING | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
152 | H | LIFS | 6277 | FH097 | LAB FURNISHING | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
153 | H | LIFS | 6278 | FH103 | MORGAN & GRUNDY | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
154 | H | LIFS | 6279 | FH104 | MORGAN & GRUNDY | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
155 | H | LIFS | 6286 | FH106 | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
156 | H | LIFS | 6287 | FH107 | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
157 | H | LIFS | 6288 | FH108 | MORGAN & GRUNDY | 1500 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
158 | H | LIFS | 6293 | FH110 | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
159 | H | LIFS | 6294 | FH086 | MORGAN & GRUNDY | 1500 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
160 | H | LIFS | 6295B | FH113 | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
161 | H | LIFS | 6296 | FH114 | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
162 | H | LIFS | 6306 | FC055 | LAB FURNISHING | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
163 | H | LIFS | 6311 | FH115 | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
164 | H | LIFS | 6312 | FH134 | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
165 | H | LIFS | 6313 | FH043 | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220.275
166 | H | LIFS | 6314A | FH102 | LAB FURNISHING | 2400 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 108 | 100mm | 522.225
167 | H | LIFS | 6318 | FH092 | KOTTERMAN | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 269.5
168 | H | LIFS | 6319 | FC037 | LAB FURNISHING | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
169 | H | LIFS | 6320 | FH293 | WALDNER | 1500 | EF-H-152-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 238.7
170 | K | CBE | 7101 | FC028 | LAB FURNISHING | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
171 | K | CBE | 7102 | FH083 | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5
172 | K | CBE | 7102 | FH177 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
173 | K | CBE | 7103 | FH247 | KEWAUNE | 1800 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 403.425 | 1 | Y
174 | K | CBE | 7103 | FH248 | KEWAUNE | 1800 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 403.425 | 1 | Y
175 | K | CBE | 7104 | FC038 | CLEAN AIR | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
176 | K | CBE | 7104 | FH050 | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5
177 | K | CBE | 7106 | FH506 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
178 | K | CBE | 7107 | FH256 | WALDNER | 1500 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
179 | K | CBE | 7107 | FH302 | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
180 | K | CBE | 7107 | FH326 | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
181 | L | CBE | 7108 | FH257 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
182 | L | CBE | 7108 | FH258 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
183 | L | CBE | 7109 | FH259 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
184 | L | CBE | 7109 | FH260 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
185 | L | CBE | 7110 | FH261 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
186 | L | CBE | 7111 | FH032 | MORGAN & GRUNDY | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
187 | L | CBE | 7111 | FH031 | MORGAN & GRUNDY | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
188 | L | CBE | 7112 | FH085 | KOTTRERMAN | 1500 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5 | 1 | Y
189 | L | CBE | 7112 | FH091 | KOTTRERMAN | 1500 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5 | 1 | Y
190 | L | CBE | 7118 | FH262 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
191 | L | CHEM | 7121 | FH042 | MORGAN & GRUNDY | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
192 | L | CHEM | 7122 | FH263 | LABCONKO | 1800 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 304.15
193 | L | CHEM | 7122 | FH264 | THERMO- FISHER | 1800 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 308
194 | L | CHEM | 7122A | FH100 | MORGAN & GRUNDY | 2100 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 95 | 100mm | 445.5 | 1 | Y
195 | L | CHEM | 7122A | FH023 | KOTTERMAN | 1800 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325.325
196 | L | CHEM | 7130 | FH044 | MORGAN & GRUNDY | 1200 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220.275 | 1 | Y
197 | L | CHEM | 7130 | FH079 | MORGAN & GRUNDY | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
198 | L | CHEM | 7132 | FH046 | WALDNER | 1500 | EF-L-157-102A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 238.7 | 1 | N (Wait for Budget)
199 | L | CHEM | 7132 | FH272 | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
200 | L | CHEM | 7132 | FH722 | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
201 | L | CHEM | 7132 | FH723 | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
202 | L | CHEM | 7133 | FC048 | LAB FURNISHING | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
203 | L | CHEM | 7133 | FH033 | MORGAN & GRUNDY | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
204 | L | CHEM | 7133 | FH045 | MORGAN & GRUNDY | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
205 | L | CHEM | 7134 | FH048 | MORGAN & GRUNDY | 1200 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220.275 | 1 | Y
206 | L | CHEM | 7135 | FH255 | MOTT | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
207 | L | CHEM | 7136 | FH049 | MORGAN & GRUNDY | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
208 | L | CHEM | 7137 | FH195 | MOTT | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
209 | L | CHEM | 7139 | FH053 | KOTTRERMAN | 1500 | EF-L-157-103A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5 | 1 | Y
210 | L | CHEM | 7139 | FH054 | KOTTRERMAN | 1500 | EF-L-157-103A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5 | 1 | Y
211 | L | CHEM | 7139 | FH062 | KOTTRERMAN | 1500 | EF-L-157-103A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 269.5
212 | L | BRI | 7152 | FH192 | MOTT | 1800 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 393.525 | 1 | Y
213 | L3 | CHEM | 7153 | FH719 | WALDNER | 1200 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 159.5 | 1 | N (Wait for Budget)
214 | L3 | CHEM | 7153 | FH720 | WALDNER | 1500 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
215 | L3 | CHEM | 7153 | FH721 | WALDNER | 1500 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
216 | L3 | CHEM | 7161C | FH307 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
217 | L3 | CHEM | 7161A | FH308 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
218 | L3 | CHEM | 7161A | FH309 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
219 | L3 | CHEM | 7161C | FH306 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
220 | L3 | CHEM | 7162 | FH304 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
221 | L3 | CHEM | 7162 | FH305 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
222 | L3 | MNF | 7163 | FH310 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
223 | L3 | MNF | 7163 | FH311 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
224 | L3 | IAS | 7164 | FH303 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
225 | L3 | IAS | 7165 | FH313 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
226 | L3 | CHEM | 7166 | FH275 | WALDNER | 1500 | EF-L3-157-107/108 | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
227 | L3 | CHEM | 7166 | FH276 | WALDNER | 1500 | EF-L3-157-107/108 | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 170.5 | 1 | N (Wait for Budget)
228 | L3 | CHEM | 7166 | FH434 | CLEAN AIR | 1500 | EF-L3-157-107/108 | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
229 | L3 | CHEM | 7166 | FH435 | CLEAN AIR | 1500 | EF-L3-157-107/108 | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
230 | L3 | CHEM | 7166 | FH436 | CLEAN AIR | 1500 | EF-L3-157-107/108 | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
231 | L3 | LIFS | 7167 | FH314 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
232 | J | CBE | 7250 | FH232 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
233 | J | CBE | 7250 | FH233 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
234 | J | CBE | 7252 | FH235 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
235 | J | CBE | 7252 | FH234 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
236 | J | CBE | 7253 | FH236 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
237 | J | CBE | 7253 | FH237 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275 | 1 | Y
238 |  | LIFS | CML | FH227 | CHEMFAST | 1200 |  | DUCTLESS |  |  |  | Y | N | N | 0.35M/S at 200mm sash height | N/A | N/A | N/A
239 |  | LIFS | CML | FH268 | CHEMFAST | 1500 |  | DUCTLESS |  |  |  | Y | N | N | 0.35M/S at 200mm sash height | N/A | N/A | N/A
240 | K | MAE | G031A | FH182 | MORGAN & GRUNDY | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
241 | K | MAE | G031A | FH315 | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319.275
136

## CYT
| Zone | Dept | Rm | FH No. | Brand | SIZE(MM) | FAN | Type | CAV (Y/N) | VAV (Y/N) | AUTO-SASH | Normal Flow (Y/N) | Low Flow (Y/N) | Extra-Low Flow (Y/N) | Acceptable Range of Face Velocity | min flow (L/S) | Maximum Sash Hieght of Fume Hoods with a Minimum Flow Rate | Max flow rate | Occupancy Data in BMS (Y-1/N) | Calibration Check (Y/N) | Notes
1 | CYT | CHEM | UG002 | FH401 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
2 | CYT | CHEM | UG002 | FH402 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
3 | CYT | CHEM | UG002 | FH403 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
4 | CYT | CHEM | UG001 | FH404 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
5 | CYT | CHEM | UG001 | FH405 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
6 | CYT | CHEM | UG001 | FH406 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
7 | CYT | CHEM | UG001 | FH412 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
8 | CYT | CHEM | UG001 | FH418 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
9 | CYT | CHEM | UG001 | FH437 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
10 | CYT | SENG | 1002 | FH505 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
11 | CYT | CHEM | 1003 | FH407 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
12 | CYT | CHEM | 1003 | FH408 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
13 | CYT | CHEM | 1003 | FH409 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
14 | CYT | CHEM | 1003 | FH410 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
15 | CYT | CHEM | 1003 | FH411 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
16 | CYT | CHEM | 1003 | FH413 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
17 | CYT | CHEM | 1003 | FH414 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
18 | CYT | CHEM | 1003 | FH415 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
19 | CYT | CHEM | 1003 | FH416 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
20 | CYT | CHEM | 1003 | FH417 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
21 | CYT | CHEM | 1003 | FH419 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
22 | CYT | CHEM | 1003 | FH420 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
23 | CYT | CHEM | 1003 | FH421 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
24 | CYT | CHEM | 1003 | FH422 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
25 | CYT | CHEM | 1003 | FH423 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
26 | CYT | CHEM | 1003 | FH424 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
27 | CYT | CHEM | 1003 | FH425 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
28 | CYT | CHEM | 1003 | FH426 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
29 | CYT | CHEM | 1003 | FH427 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
30 | CYT | CHEM | 1004 | FH428 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
31 | CYT | CHEM | 1004 | FH429 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
32 | CYT | CHEM | 1004 | FH430 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
33 | CYT | CHEM | 1004 | FH431 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
34 | CYT | CHEM | 1004 | FH432 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
35 | CYT | CHEM | 1004 | FH433 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
36 | CYT | CHEM | 1004 | FH441 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
37 | CYT | CHEM | 1004 | FH442 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198
38 | CYT | CBME | 2007 | FH444 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
39 | CYT | CBME | 2007 | FH445 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
40 | CYT | CBME | 2007 | FH446 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
41 | CYT | CBME | 2007 | FH447 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
42 | CYT | CBME | 2007A | FH453 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
43 | CYT | CBME | 2007B | FH448 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
44 | CYT | CBME | 2007B | FH449 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
45 | CYT | BME | 3007E | FH452 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
46 | CYT | ECE | 3014C | FH455 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
47 | CYT | ECE | 3014D | FH454 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
48 | CYT | EI | 4007 | FH456 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
49 | CYT | EI | 4007 | FH457 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
50 | CYT | EI | 4007 | FH458 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
51 | CYT | EI | 4007 | FH459 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
52 | CYT | EI | 4007 | FH460 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
53 | CYT | MAE | 4007C | FH461 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
54 | CYT | MAE | 4007C | FH462 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
55 | CYT | EI | 4007 | FH510 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
56 | CYT | EI | 4007 | FH511 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
57 | CYT | EI | 4007 | FH526 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
58 | CYT | EI | 4007 | FH532 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
59 | CYT | ECE | 4014 | FH463 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
60 | CYT | ECE | 4014 | FH464 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
61 | CYT | ECE | 4014 | FH465 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
62 | CYT | ECE | 4014 | FH466 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
63 | CYT | ECE | 4014 | FH467 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
64 | CYT | ECE | 4014 | FH468 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
65 | CYT | ECE | 4014 | FH469 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
66 | CYT | ECE | 4014 | FH450 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
67 | CYT | ECE | 4014 | FH451 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
68 | CYT | ECE | 4014 | FH600 | Waldner | 1800 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 81 | 100mm | 212
69 | CYT | LIFS | 5007 | FH470 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
70 | CYT | LIFS | 5007 | FH471 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
71 | CYT | LIFS | 5007 | FH472 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
72 | CYT | LIFS | 5014 | FH473 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
73 | CYT | LIFS | 5014 | FH474 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
74 | CYT | LIFS | 5014 | FH477 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
75 | CYT | LIFS | 5014 | FH478 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
76 | CYT | LIFS | 5014 | FH479 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
77 | CYT | LIFS | 5014 | FH480 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
78 | CYT | LIFS | 5014 | FH481 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
79 | CYT | LIFS | 5014 | FH482 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
80 | CYT | LIFS | 5014 | FH483 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
81 | CYT | LIFS | 5014 | FH484 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
82 | CYT | CHEM | 6007 | FH065 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
83 | CYT | CHEM | 6007 | FH066 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
84 | CYT | CHEM | 6007 | FH072 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
85 | CYT | CHEM | 6007 | FH240 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
86 | CYT | CHEM | 6007 | FH438 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Yes
87 | CYT | CHEM | 6007 | FH439 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Yes
88 | CYT | CHEM | 6007 | FH440 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Yes
89 | CYT | CHEM | 6007 | FH443 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Yes
90 | CYT | CHEM | 6007 | FH485 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
91 | CYT | CHEM | 6007 | FH486 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
92 | CYT | CHEM | 6007 | FH487 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
93 | CYT | CHEM | 6007 | FH489 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
94 | CYT | CHEM | 6007 | FH490 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
95 | CYT | CHEM | 6007 | FH496 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
96 | CYT | CHEM | 6007 | FH497 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
97 | CYT | CHEM | 6007 | FH498 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
98 | CYT | CHEM | 6007 | FH499 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
99 | CYT | CHEM | 6007 | FH500 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
100 | CYT | CHEM | 6007 | FH501 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
101 | CYT | CHEM | 6007 | FH502 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
102 | CYT | CHEM | 6007 | FH503 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
103 | CYT | CHEM | 6007 | FH504 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
104 | CYT | CHEM | 6007 | FH507 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
105 | CYT | CHEM | 6007A | FH508 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
106 | CYT | CHEM | 6007 | FH601 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
107 | CYT | CHEM | 6007 | FH602 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
108 | CYT | CHEM | 6007 | FH603 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
109 | CYT | CHEM | 6007 | FH604 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
110 | CYT | CHEM | 6014A | FH063 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
111 | CYT | CHEM | 6014 | FH064 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
112 | CYT | CHEM | 6014 | FH068 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
113 | CYT | CHEM | 6014 | FH070 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
114 | CYT | CHEM | 6014 | FH512 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
115 | CYT | CHEM | 6014 | FH513 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
116 | CYT | CHEM | 6014 | FH514 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
117 | CYT | CHEM | 6014 | FH515 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
118 | CYT | CHEM | 6014 | FH516 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
119 | CYT | CHEM | 6014 | FH518 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
120 | CYT | CHEM | 6014 | FH519 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
121 | CYT | CHEM | 6014 | FH521 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
122 | CYT | CHEM | 6014 | FH522 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
123 | CYT | CHEM | 6014 | FH523 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
124 | CYT | CHEM | 6014 | FH524 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
125 | CYT | CHEM | 6014 | FH525 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
126 | CYT | CHEM | 6014 | FH528 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
127 | CYT | CHEM | 6014 | FH529 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
128 | CYT | CHEM | 6014 | FH530 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
129 | CYT | CHEM | 6014 | FH531 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Yes
130 | CYT | CHEM | 6014 | FH605 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
131 | CYT | CHEM | 6014 | FH606 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
132 | CYT | CHEM | 6014 | FH607 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
133 | CYT | CHEM | 6014 | FH608 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
134 | CYT | CHEM | 6014 | FH609 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
135 | CYT | CHEM | 6014 | FH610 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
136 | CYT | CHEM | 6014 | FH611 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
137 | CYT | CHEM | 6014 | FH612 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | Yes
56

## HSEO Combine List
Zone | DEPT | Rm | FH No. | Occupancy Data in BMS (Y-1/N) | Calibration Check (Y/N) for Occupancey | Notes | BRAND | SIZE(MM) | VS FAN | Type | CAV (Y/N) | VAV (Y/N) | AutoSash | Normal Flow (Y/N) | Low Flow (Y/N) | Extra-Low Flow (Y/N) | Acceptable Range of Face Velocity | min flow (L/S) | Maximum Sash Hieght of Fume Hoods with a Minimum Flow Rate | Max flow rate | sash unit/range
K | ECE | 1043 | FH167 |  |  |  | MORGAN & GRUNDY | 1200 | EF-ENT-140-4 | BBQ | Y | N |  | N | N | N | N/A | N/A | N/A | N/A
K | ECE | 1047A | FH161 |  |  |  | MORGAN & GRUNDY | 1500 | EF-ENT-140-4 | BBQ | Y | N |  | N | N | N | N/A | N/A | N/A | N/A
K | ECE | 1047A | FH162 |  |  |  | MORGAN & GRUNDY | 1500 | EF-ENT-140-4 | BBQ | Y | N |  | N | N | N | N/A | N/A | N/A | N/A
K | ECE | 1047A | FH163 |  |  |  | MORGAN & GRUNDY | 1500 | EF-ENT-140-4 | BBQ | Y | N |  | N | N | N | N/A | N/A | N/A | N/A
K | ECE | 1047A | FH170 |  |  |  | MORGAN & GRUNDY | 1200 | EF-ENT-140-4 | BBQ | Y | N |  | N | N | N | N/A | N/A | N/A | N/A
J | CIVL | 1207C | FH291 |  |  |  | RENGGLI | 1500 | EF-J-152-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 201
J | CIVL | 1209C | FH294 |  |  |  | WALDNER | 1500 | EF-J-152-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 239
J | CIVL | 1211 | FH226 |  |  |  | LAB FURNISHING | 1500 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
J | MAE | 1213 | FH265 |  |  |  | KEWAUNE | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 228
J | CLS | 1215 | FH119 |  |  |  | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
K | CHEM | 2123 | FC041 |  |  |  | LAB FURNISHING | 1500 | EF-K-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
L | MCPF | 2151 | FH178 | 1 | Y | 1001.BV1 | MORGAN & GRUNDY | 1500 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-450mm
L | CAMP | 2162A | FH324 |  |  |  | MOTT | 1500 | EF-L3-157-107/108 | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319
L | ECE | 2164 | FH475 |  |  |  | CLEAN AIR | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-750mm
L | ECE | 2166 | FC042 |  |  |  | LAB FURNISHING | 1500 | EF-L3-157-107/108 | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
L | ECE | 2166 | FC054 |  |  |  | LAB FURNISHING | 1200 | EF-L3-157-107/108 | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | ECE | 2227 | FC031 |  |  |  | LAB FURNISHING | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
H | CHEM | 2228 | FH710 |  |  |  | CHEMFAST | 1200 |  | DUCTLESS |  |  |  | Y | N | N | 0.35M/S at 200mm sash height | N/A | N/A | N/A
H | CHEM/LIFS | 2229 | FC053 |  |  |  | LAB FURNISHING | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | LIFS | 2230K | FH290 |  |  |  | WALDNER | 1200 | EF-H-152-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160
H | PHYS | 2232 | FC002 |  |  |  | LAB FURNISHING | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | ECE | 2234 | FH253 |  |  |  | MOTT | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319
H | PHYS | 2237 | FH724 |  |  |  | WALDNER | 1500 | EF-H-152-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171
K | HSEO | 3107 | FC030 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-K-157-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 239 | mm
K | HSEO | 3107D | FC003 | 1 | Y | 5302.BV3 | LAB FURNISHING | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 50-500mm
K | HSEO | 3107 | FC029 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-K-157-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 239 | mm
L | ECE | 3112 | FC004 | 1 | Y | 5303.BV3 | LAB FURNISHING | 1200 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 50-500mm
L | ECE | 3112 | FC040 | 1 | Y | 5303.BV6 | LAB FURNISHING | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
L | ECE | 3125B | FH245 |  |  |  | ESCO | 1200 |  | DUCTLESS |  |  |  | Y | N | N | 0.35M/S at 200mm sash height | N/A | N/A | N/A
J | CIVL | 3201 | FH705 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
J | CIVL | 3201 | FH706 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
J | CIVL | 3201 | FH707 |  |  |  | RENGGLI | 1500 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 201 | 0-500mm
J | CIVL | 3202 | FH704 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
J | CIVL | 3212 | FH271 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
H | NFF | 3231 | FC009 |  |  |  | LAB FURNISHING | 1200 | EF-H-152-105A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
K | ENVR | 4094 | FH488 |  |  |  | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
K | ENVR | 4094 | FH494 |  |  |  | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
K | ENVR | 4094 | FH517 |  |  |  | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
K | ENVR | 4094 | FH520 |  |  |  | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
K | ENVR | 4096 | FH076 |  |  |  | WALDNER | 1500 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | no sash point
K | ENVR | 4105 | FH491 |  |  |  | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
K | ENVF | 4109C | FH067 |  |  |  | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | no sash point
K | ENVF | 4109C | FH069 |  |  |  | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | no sash point
K | ENVR | 4110 | FH527 |  |  |  | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
K | ENVR | 4111 | FH495 | 1 | Y | 415.BV1 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
K | ENVR | 4113 | FH301 | 1 | Y | 417.BV3 | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
K | ENVR | 4114 | FH251 | 1 | Y | 416.BV3 | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L | PHYS | 4115 | FH277 | 1 | N (Wait for Budget) |  | WALDNER | 1200 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | mm
L | PHYS | 4115A | FH278 | 1 | N (Wait for Budget) |  | WALDNER | 1200 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | mm
L | PHYS | 4115D | FH281 |  |  |  | RENGGLI | 1200 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 0-500mm
L | PHYS | 4116A | FH279 | 1 | N (Wait for Budget) |  | WALDNER | 1200 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | mm
L | PHYS | 4116B | FH282 |  |  |  | RENGGLI | 1200 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 0-500mm
L | PHYS | 4117 | FH280 | 1 | N (Wait for Budget) |  | WALDNER | 1200 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | mm
L | PHYS | 4118 | FH005 | 1 | Y | 1201.BV3 | MORGAN & GRUNDY | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-480mm
L | PHYS | 4119B | FH181 | 1 | Y | 1201.BV6 | LAB FURNISHING | 1200 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220
L | PHYS | 4121B | FH006 | 1 | Y | 1201.BV9 | MORGAN & GRUNDY | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-480mm
L | PHYS | 4123 | FH007 | 1 | Y | 1202.BV3 | MORGAN & GRUNDY | 1200 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 50-500mm
L | PHYS | 4125 | FH286 |  |  |  | RENGGLI | 1200 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160
L | PHYS | 4125 | FH287 |  |  |  | RENGGLI | 1200 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160
L | PHYS | 4126 | FH008 | 1 | Y | 1202.BV6 | MORGAN & GRUNDY | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
L | PHYS | 4139 | FH010 | 1 | Y | 1204.BV6 | LAB FURNISHING | 1200 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 50-500mm
L | PHYS | 4141 | FH011 | 1 | Y | 1204.BV9 | MORGAN & GRUNDY | 1200 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 50-500mm
L | PHYS | 4142 | FH292 |  |  |  | RENGGLI | 1500 | EF-L-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 201
|  | 4142 | FH172 |  |  | 1204.BV12 | Removed
L | PHYS | 4145 | FH206 | 1 | NIL |  | NUAIRE | 1800 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 264 | no sash point
L | PHYS | 4145 | FH231 | 1 | Y | 1205.BV3 | APMG | 1200 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 235 | 50-500mm
L | BRI | 4150 | FH273 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L | BRI | 4150 | FH274 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L3 | LIFS | 4160 | FH332 | 1 | Y | 184.BV3 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | LIFS | 4160 | FH333 | 1 | Y | 184.BV1 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | LIFS | 4160B | FH331 | 1 | Y | 167.BV1 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
J | LIFS | 4218 | FH283 |  |  |  | CHEMFAST | 1500 |  | DUCTLESS |  |  |  | Y | N | N | 0.35M/S at 200mm sash height | N/A | N/A | N/A
H | MAE | 4222 | FH254 |  |  |  | MOTT | 1500 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319
H | MAE | 4222B | FH266 |  |  |  | WALDNER | 1500 | EF-H-152-06 | BBQ | Y | N | Y | N | N | N | N/A | N/A | N/A | N/A
H | MAE | 4225 | FH476 |  |  |  | CLEAN AIR | 1500 | EF-H-152-102A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
H | MAE | 4225 | FH493 |  |  |  | CLEAN AIR | 1500 | EF-H-152-102A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
H | MAE | 4225 | FH243 |  |  |  | KEWAUNE | 1500 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 327
H | MAE | 4225 | FH252 |  |  |  | MOTT | 1500 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319
H | MAE | 4227 | FH330 |  |  |  | MOTT | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319
H | AEMF | 4228 | FH055 |  |  |  | KEWAUNE | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 327
H | AEMF | 4229 | FC026 |  |  |  | LAB FURNISHING | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | AEMF | 4229 | FC049 |  |  |  | LAB FURNISHING | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
H | AEMF | 4229 | FH169 |  |  |  | MORGAN & GRUNDY | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
H | AEMF | 4229 | FH075 |  |  |  | MORGAN & GRUNDY | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
K | EVNG | 6102 | FC018 | 1 | Y | 628.BV3 | LAB FURNISHING | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 50-500mm
K | FMO/DMSF | 6103 | FC017 | 1 | Y | 628.BV6 | LAB FURNISHING | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 50-500mm
K | CBE | 6104 | FH230 | 1 | Y | 628.BV9 | APMG | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 235 | 50-500mm
K | MAE | 6105 | FC019 | 1 | Y | 629.BV9 | LAB FURNISHING | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 50-500mm
K | MAE | 6105 | FC020 | 1 | Y | 629.BV3 | LAB FURNISHING | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 50-500mm
K | CLS | 6109 | FH318 |  |  |  | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319
K | CBE | 6113 | FH051 | 1 | Y | 630.BV3 | KOTTERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 0-500mm
K | CBE | 6114 | FH084 | 1 | Y | 601.BV7 | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 50-500mm
K | CBE | 6114 | FH025 | 1 | Y | 630.BV12 | KOTTERMAN | 1800 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325 | 50-500mm
|  | 6114 | FH165 |  |  | 630.BV6 | Removed
K | CBE | 6115 | FH269 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-K-157-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 239 | mm
K | CBE | 6115 | FH270 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-K-157-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 239 | mm
L | CBE | 6117 | FH285 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L | CBE | 6118 | FH059 | 1 | Y | 635.BV3 | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 0-500mm
L | CBE | 6119 | FH078 | 1 | Y | 635.BV6 | KOTTRERMAN | 1500 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 50-600mm
L | CHEM | 6120 | FH017 | 1 | Y | 603.BV13 | LAB FURNISHING | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
L | CHEM | 6120 | FC032 | 1 | Y | 604.BV1 | LAB FURNISHING | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
L | CBE | 6121 | FH061 | 1 | Y | 636.BV3 | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 50-600mm
L | CHEM | 6122 | FH018 | 1 | Y | 603.BV1 | LAB FURNISHING | 1800 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 374 | 50-500mm
L | CHEM | 6122 | FH020 | 1 | Y | 603.BV7 | KOTTRERMAN | 1500 | EF-L-157-102A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 50-630mm
L | CHEM | 6122 | FH021 | 1 | Y | 603.BV10 | KOTTRERMAN | 1500 | EF-L-157-102A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 50-500mm
L | CHEM | 6122 | FH041 | 1 | Y | 603.BV4 | KOTTRERMAN | 1800 | EF-L-157-102A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325 | 50-500mm
L | CHEM | 6124B | FH026 |  |  |  | WALDNER | 1800 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 81 | 100mm | 212 | 50-500mm
L | CHEM | 6124B | FH288 |  |  |  | RENGGLI | 1200 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 0-500mm
L | CHEM | 6124B | FH289 |  |  |  | RENGGLI | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 201 | 0-500mm
L | CHEM | 6124B | FH039 |  |  |  | WALDNER | 1800 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 81 | 100mm | 212 | no sash point
L | CHEM | 6125 | FH022 | 1 | Y | 624.BV5 | KOTTERMAN | 1800 | EF-L-157-102A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325 | 50-500mm
L | CHEM | 6125 (6124) | FH024 | 1 | Y | 625.BV5 | KOTTERMAN | 1800 | EF-L-157-102A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325 | 50-500mm
L | CHEM | 6125 | FH040 |  |  |  | KOTTERMAN | 1800 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325 | no sash point
L | CHEM | 6125 | FH700 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L | CHEM | 6125 | FH701 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L | CHEM | 6125 | FH702 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L | CHEM | 6125 | FH703 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L | BCRF | 6127 | FH209 | 1 | Y | 608.BV6 | CMS | 1200 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 245 | 50-500mm
L | PHYS | 6138 | FH028 | 1 | Y | 631.BV3 | MORGAN & GRUNDY | 1200 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | mm
L | BRI | 6141 | FH191 | 1 | Y | 606.BV1 | MOTT | 1800 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 396 | mm
L3 | CHEM | 6143 | FH321 | 1 | Y | 227.BV1 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | CHEM | 6143 | FH322 | 1 | Y | 227.BV3 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | CCM | 6145 | FH319 | 1 | Y | 228.BV1 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | CCM | 6145 | FH320 | 1 | Y | 228.BV3 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | BCRF | 6146 | FH325 | 1 | Y | 229.BV1 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | R&D | 6147 | FH317 | 1 | Y | 277.BV3 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | FINTEX | 6148 | FH327 | 1 | Y | 278.BV3 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | FINTEX | 6148 | FH328 | 1 | Y | 278.BV1 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | NAMI | 6149 | FH708 | 1 | NIL |  | RENGGLI | 1200 | EF-L3-157-107/108 | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 0-500mm
L3 | NAMI | 6149 | FH709 | 1 | NIL |  | RENGGLI | 1200 | EF-L3-157-107/108 | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 0-500mm
L3 | NAMI | 6150 | FH323 | 1 | Y | 279.BV1, 280.BV1 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 35-500mm
J | LIFS | 6201 | FH711 | 1 | N (Wait for Budget) |  | WALDNER | 1200 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | mm
J | LIFS | 6201 | FH712 | 1 | N (Wait for Budget) |  | WALDNER | 1200 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | mm
J | LIFS | 6201 | FH713 | 1 | N (Wait for Budget) |  | WALDNER | 1200 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | mm
J | LIFS | 6201 | FH714 | 1 | N (Wait for Budget) |  | WALDNER | 1200 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | mm
J | LIFS | 6219 | FH145 |  |  |  | MORGAN & GRUNDY | 1200 | EF-J-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
J | LIFS | 6220 | FH144 |  |  |  | MORGAN & GRUNDY | 1200 | EF-J-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
J | LIFS | 6221 | FH166 |  |  |  | MORGAN & GRUNDY | 1200 | EF-J-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
J | LIFS | 6223 | FH143 |  |  |  | MORGAN & GRUNDY | 1200 | EF-J-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
J | LIFS | 6224 | FH142 |  |  |  | MORGAN & GRUNDY | 1200 | EF-J-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
J | LIFS | 6225 | FH138 |  |  |  | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
J | LIFS | 6231 | FH140 |  |  |  | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
J | LIFS | 6233A | FC010 |  |  |  | LAB FURNISHING | 1500 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
J | LIFS | 6233B | FH137 |  |  |  | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
J | LIFS | 6237 | FH135 |  |  |  | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
J | LIFS | 6243 | FH136 |  |  |  | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
J | LIFS | 6244 | FH132 |  |  |  | LAB FURNISHING | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
J | LIFS | 6246 | FH130 |  |  |  | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
J | LIFS | 6248 | FH129 |  |  |  | LAB FURNISHING | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
J | LIFS | 6255 | FH267 |  |  |  | MOTT | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 245
J | LIFS | 6256A | FC056 |  |  |  | LAB FURNISHING | 1200 |  | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
J | LIFS | 6260 | FH312 |  |  |  | MOTT | 1500 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319
H | LIFS | 6274 | FH099 |  |  |  | LAB FURNISHING | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | LIFS | 6277 | FH097 |  |  |  | LAB FURNISHING | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | LIFS | 6278 | FH103 |  |  |  | MORGAN & GRUNDY | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | LIFS | 6279 | FH104 |  |  |  | MORGAN & GRUNDY | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | LIFS | 6286 | FH106 |  |  |  | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | LIFS | 6287 | FH107 |  |  |  | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | LIFS | 6288 | FH108 |  |  |  | MORGAN & GRUNDY | 1500 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
H | LIFS | 6293 | FH110 |  |  |  | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | LIFS | 6294 | FH086 |  |  |  | MORGAN & GRUNDY | 1500 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
H | LIFS | 6295B | FH113 |  |  |  | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | LIFS | 6296 | FH114 |  |  |  | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | LIFS | 6306 | FC055 |  |  |  | LAB FURNISHING | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | LIFS | 6311 | FH115 |  |  |  | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | LIFS | 6312 | FH134 |  |  |  | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | LIFS | 6313 | FH043 |  |  |  | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
H | LIFS | 6314A | FH102 |  |  |  | LAB FURNISHING | 2400 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 108 | 100mm | 522
H | LIFS | 6318 | FH092 |  |  |  | KOTTERMAN | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 270
H | LIFS | 6319 | FC037 |  |  |  | LAB FURNISHING | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
H | LIFS | 6320 | FH293 |  |  |  | WALDNER | 1500 | EF-H-152-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 239
K | CBE | 7101 | FC028 | 1 | Y | 1146.BV3 | LAB FURNISHING | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
K | CBE | 7102 | FH083 |  |  |  | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270
K | CBE | 7102 | FH177 | 1 | Y | 1147.BV3 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 40-470mm
K | CBE | 7103 | FH247 | 1 | Y | 1146.BV9 | KEWAUNE | 1800 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 403 | 50-500mm
K | CBE | 7103 | FH248 | 1 | Y | 1146.BV12 | KEWAUNE | 1800 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 403 | 50-500mm
K | CBE | 7104 | FC038 | 1 | Y | 1142.BV3 | CLEAN AIR | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 50-500mm
K | CBE | 7104 | FH050 |  |  |  | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270
K | CBE | 7106 | FH506 | 1 | Y | 1142.BV9 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
K | CBE | 7107 | FH256 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 0-1000mm
K | CBE | 7107 | FH302 | 1 | Y | 1127.BV3 | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
K | CBE | 7107 | FH326 | 1 | Y | 1141.BV3 | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 35-500mm
L | CBE | 7108 | FH257 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L | CBE | 7108 | FH258 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L | CBE | 7109 | FH259 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L | CBE | 7109 | FH260 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L | CBE | 7110 | FH261 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L | CBE | 7111 | FH032 | 1 | Y | 1121.BV4 | MORGAN & GRUNDY | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-480mm
L | CBE | 7111 | FH031 | 1 | Y | 1121.BV1 | MORGAN & GRUNDY | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
L | CBE | 7112 | FH085 | 1 | Y | 1121.BV10 | KOTTRERMAN | 1500 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 100-600mm
L | CBE | 7112 | FH091 | 1 | Y | 1121.BV7 | KOTTRERMAN | 1500 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 100-600mm
L | CBE | 7118 | FH262 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L | CHEM | 7121 | FH042 | 1 | Y | 1118.BV13 | MORGAN & GRUNDY | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
L | CHEM | 7122 | FH263 |  |  |  | LABCONKO | 1800 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 304
L | CHEM | 7122 | FH264 | 1 | Y | 1118.BV7 | THERMO- FISHER | 1800 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 308 | 50-500mm
L | CHEM | 7122A | FH100 | 1 | Y | 1117.BV1 | MORGAN & GRUNDY | 2100 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 95 | 100mm | 446 | 50-500mm
L | CHEM | 7122A | FH023 |  |  |  | KOTTERMAN | 1800 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325
L | CHEM | 7130 | FH044 | 1 | Y | 1111.BV1 | MORGAN & GRUNDY | 1200 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 50-500mm
L | CHEM | 7130 | FH079 |  |  |  | MORGAN & GRUNDY | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
L | CHEM | 7132 | FH046 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-102A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 239 | mm
L | CHEM | 7132 | FH272 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L | CHEM | 7132 | FH722 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L | CHEM | 7132 | FH723 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L | CHEM | 7133 | FC048 | 1 | Y | 1112.BV1 | LAB FURNISHING | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
L | CHEM | 7133 | FH033 | 1 | Y | 1112.BV4 | MORGAN & GRUNDY | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-480mm
L | CHEM | 7133 | FH045 | 1 | Y | 1112.BV7 | MORGAN & GRUNDY | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
L | CHEM | 7134 | FH048 | 1 | Y | 1110.BV1 | MORGAN & GRUNDY | 1200 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 50-500mm
L | CHEM | 7135 | FH255 | 1 | Y | 1130.BV1 | MOTT | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L | CHEM | 7136 | FH049 | 1 | Y | 1109.BV1 | MORGAN & GRUNDY | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-480mm
L | CHEM | 7137 | FH195 | 1 | Y | 1108.BV4 | MOTT | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L | CHEM | 7139 | FH053 | 1 | Y | 1106.BV1 | KOTTRERMAN | 1500 | EF-L-157-103A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 50-600mm
L | CHEM | 7139 | FH054 | 1 | Y | 1106.BV13 | KOTTRERMAN | 1500 | EF-L-157-103A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 50-600mm
L | CHEM | 7139 | FH062 | 1 | Y | 1106.BV10 | KOTTRERMAN | 1500 | EF-L-157-103A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 60-600mm
L | BRI | 7152 | FH192 | 1 | Y | 1101.BV10 | MOTT | 1800 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 394 | 50-500mm
L3 | CHEM | 7153 | FH719 | 1 | N (Wait for Budget) |  | WALDNER | 1200 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | mm
L3 | CHEM | 7153 | FH720 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L3 | CHEM | 7153 | FH721 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L3 | CHEM | 7161C | FH307 | 1 | Y | 328.BV5 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319
L3 | CHEM | 7161A | FH308 | 1 | Y | 328.BV1 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | CHEM | 7161A | FH309 | 1 | Y | 328.BV3 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | CHEM | 7161C | FH306 | 1 | Y | 328.BV7 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | CHEM | 7162 | FH304 | 1 | Y | 327.BV1 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | CHEM | 7162 | FH305 | 1 | Y | 327.BV3 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | MNF | 7163 | FH310 | 1 | Y | 326.BV3 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 35-500mm
L3 | MNF | 7163 | FH311 | 1 | Y | 326.BV1 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 35-500mm
L3 | IAS | 7164 | FH303 | 1 | Y | 376.BV3 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | IAS | 7165 | FH313 | 1 | Y | 375.BV3 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
L3 | CHEM | 7166 | FH275 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L3-157-107/108 | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L3 | CHEM | 7166 | FH276 | 1 | N (Wait for Budget) |  | WALDNER | 1500 | EF-L3-157-107/108 | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | mm
L3 | CHEM | 7166 | FH434 | 1 | NIL |  | CLEAN AIR | 1500 | EF-L3-157-107/108 | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 50-500mm
L3 | CHEM | 7166 | FH435 | 1 | NIL |  | CLEAN AIR | 1500 | EF-L3-157-107/108 | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 50-500mm
L3 | CHEM | 7166 | FH436 | 1 | NIL |  | CLEAN AIR | 1500 | EF-L3-157-107/108 | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 50-500mm
L3 | LIFS | 7167 | FH314 | 1 | Y | 378.BV1 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
J | CBE | 7250 | FH232 | 1 | Y | 1122.BV1 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
J | CBE | 7250 | FH233 | 1 | Y | 1122.BV4 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
J | CBE | 7252 (7253) | FH235 | 1 | Y | 1123.BV7 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
J | CBE | 7252 | FH234 | 1 | Y | 1123.BV4 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
J | CBE | 7253 | FH236 | 1 | Y | 1123.BV10 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 65-500mm
J | CBE | 7253 | FH237 | 1 | Y | 1123.BV1 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
| LIFS | CML | FH227 |  |  |  | CHEMFAST | 1200 |  | DUCTLESS |  |  |  | Y | N | N | 0.35M/S at 200mm sash height | N/A | N/A | N/A
| LIFS | CML | FH268 |  |  |  | CHEMFAST | 1500 |  | DUCTLESS |  |  |  | Y | N | N | 0.35M/S at 200mm sash height | N/A | N/A | N/A
K | MAE | G031A (G031B) | FH182 | 1 | Y | 5101.BV3 | MORGAN & GRUNDY | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 50-500mm
|  | G031D | FH83 | 1 | Y | 5101.BV6 | Changed to FH315
K | MAE | G031A | FH315 |  |  | 5101.BV6? | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 50-500mm
CYT | CHEM | UG002 | FH401 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | UG002 | FH402 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | UG002 | FH403 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | UG001 | FH404 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | UG001 | FH405 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | UG001 | FH406 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | UG001 | FH412 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | UG001 | FH418 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | UG001 | FH437 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | SENG | 1002 | FH505 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 1003 | FH407 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH408 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH409 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH410 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH411 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH413 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH414 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH415 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH416 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH417 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH419 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH420 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH421 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH422 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH423 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH424 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH425 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH426 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1003 | FH427 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1004 | FH428 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1004 | FH429 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1004 | FH430 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1004 | FH431 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1004 | FH432 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1004 | FH433 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1004 | FH441 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 1004 | FH442 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CBME | 2007 | FH444 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CBME | 2007 | FH445 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CBME | 2007 | FH446 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CBME | 2007 | FH447 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CBME | 2007A | FH453 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CBME | 2007B | FH448 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CBME | 2007B | FH449 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | BME | 3007E | FH452 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | ECE | 3014C | FH455 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | ECE | 3014D | FH454 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | EI | 4007 | FH456 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | EI | 4007 | FH457 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | EI | 4007 | FH458 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | EI | 4007 | FH459 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | EI | 4007 | FH460 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | MAE | 4007C | FH461 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | MAE | 4007C | FH462 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | EI | 4007 | FH510 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | EI | 4007 | FH511 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | EI | 4007 | FH526 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | EI | 4007 | FH532 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | ECE | 4014 | FH463 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | ECE | 4014 | FH464 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | ECE | 4014 | FH465 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | ECE | 4014 | FH466 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | ECE | 4014 | FH467 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | ECE | 4014 | FH468 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | ECE | 4014 | FH469 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | ECE | 4014 | FH450 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | ECE | 4014 | FH451 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | ECE | 4014 | FH600 |  |  |  | Waldner | 1800 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 81 | 100mm | 212
CYT | LIFS | 5007 | FH470 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | LIFS | 5007 | FH471 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | LIFS | 5007 | FH472 |  |  |  | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | LIFS | 5014 | FH473 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | LIFS | 5014 | FH474 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | LIFS | 5014 | FH477 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | LIFS | 5014 | FH478 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | LIFS | 5014 | FH479 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | LIFS | 5014 | FH480 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | LIFS | 5014 | FH481 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | LIFS | 5014 | FH482 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | LIFS | 5014 | FH483 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | LIFS | 5014 | FH484 |  |  |  | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH065 | 1 | Yes for occupancy | 9300.BV5 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6007 | FH066 | 1 | Yes for occupancy | 9300.BV8 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6007 | FH072 | 1 | Yes for occupancy | 9300.BV6 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6007 | FH240 | 1 | Yes for occupancy | 9300.BV7 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6007 | FH438 | 1 | Yes for occupancy | 100036.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 6007 | FH439 | 1 | Yes for occupancy | 100037.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 6007 | FH440 | 1 | Yes for occupancy | 100038.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 6007 | FH443 | 1 | Yes for occupancy | 100039.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | %
CYT | CHEM | 6007 | FH485 | 1 | Yes for occupancy | 100485.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH486 | 1 | Yes for occupancy | 100486.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH487 | 1 | Yes for occupancy | 100487.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH489 | 1 | Yes for occupancy | 100489.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH490 | 1 | Yes for occupancy | 100490.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH496 | 1 | Yes for occupancy | 100496.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH497 | 1 | Yes for occupancy | 100497.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH498 | 1 | Yes for occupancy | 100498.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH499 | 1 | Yes for occupancy | 100499.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH500 | 1 | Yes for occupancy | 100500.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH501 | 1 | Yes for occupancy | 100501.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH502 | 1 | Yes for occupancy | 100502.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH503 | 1 | Yes for occupancy | 100503.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH504 | 1 | Yes for occupancy | 100044.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH507 | 1 | Yes for occupancy | 100507.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007A | FH508 | 1 | Yes for occupancy | 100507.BI14 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6007 | FH601 | 1 | Yes for occupancy | 9300.BV4 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6007 | FH602 | 1 | Yes for occupancy | 9300.BV3 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6007 | FH603 | 1 | Yes for occupancy | 9300.BV2 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6007 | FH604 | 1 | Yes for occupancy | 9300.BV1 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6014A | FH063 | 1 | Yes for occupancy | 9308.BV9 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6014 | FH064 | 1 | Yes for occupancy | 9308.BV12 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6014 | FH068 | 1 | Yes for occupancy | 9308.BV9 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6014 | FH070 | 1 | Yes for occupancy | 9308.BV11 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6014 | FH512 | 1 | Yes for occupancy | 100512.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH513 | 1 | Yes for occupancy | 100513.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH514 | 1 | Yes for occupancy | 100514.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH515 | 1 | Yes for occupancy | 100515.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH516 | 1 | Yes for occupancy | 100516.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH518 | 1 | Yes for occupancy | 100518.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH519 | 1 | Yes for occupancy | 100519.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH521 | 1 | Yes for occupancy | 100521.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH522 | 1 | Yes for occupancy | 100522.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH523 | 1 | Yes for occupancy | 100523.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH524 | 1 | Yes for occupancy | 100524.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH525 | 1 | Yes for occupancy | 100525.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH528 | 1 | Yes for occupancy | 100528.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH529 | 1 | Yes for occupancy | 100529.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH530 | 1 | Yes for occupancy | 100530.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH531 | 1 | Yes for occupancy | 100531.BI14 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | %
CYT | CHEM | 6014 | FH605 | 1 | Yes for occupancy | 9308.BV3 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6014 | FH606 | 1 | Yes for occupancy | 9308.BV2 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6014 | FH607 | 1 | Yes for occupancy | 9308.BV1 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6014 | FH608 | 1 | Yes for occupancy | 9308.BV6 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6014 | FH609 | 1 | Yes for occupancy | 9308.BV4 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6014 | FH610 | 1 | Yes for occupancy | 9308.BV5 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6014 | FH611 | 1 | Yes for occupancy | 9308.BV8 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
CYT | CHEM | 6014 | FH612 | 1 | Yes for occupancy | 9308.BV7 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | mm
196