## Combine for HSEO
FH No. | DEPT | Rm | BRAND | SIZE(MM) | VS FAN | Type | CAV (Y/N) | VAV (Y/N) | AutoSash | Normal Flow (Y/N) | Low Flow (Y/N) | Extra-Low Flow (Y/N) | Acceptable Range of Face Velocity | min flow (L/S) | Maximum Sash Hieght of Fume Hoods with a Minimum Flow Rate | Max flow rate | Occupancy Data in BMS (Y-1/N) | Calibration Check (Y/N) | Notes
FC002 | PHYS | 2232 | LAB FURNISHING | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220 |  |  |  | JHL | Rm7103 | FH247* | FH247 | CBE
FC003 | HSEO | 3107D | LAB FURNISHING | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 1 | Y |  | JHL | Rm7133 | FH045* | FH045 | CHEM
FC004 | ECE | 3112 | LAB FURNISHING | 1200 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 1 | Y |  | JHL | Rm4114 | FH251* | FH251 | ENVR
FC009 | NFF | 3231 | LAB FURNISHING | 1200 | EF-H-152-105A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220 |  |  |  | JHL | Rm7130 | FH079 | FH079 | CHEM
FC010 | LIFS | 6233A | LAB FURNISHING | 1500 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297 |  |  |  | JHL | Rm4118 | FH05 | FH050 | CBE
FC017 | FMO/DMSF | 6103 | LAB FURNISHING | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 1 | Y |  | EC | Rm7166 | FH434* | FH434 | CHEM
FC018 | EVNG | 6102 | LAB FURNISHING | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 1 | Y |  | EC | Rm7166 | FH435* | FH435 | CHEM
FC019 | MAE | 6105 | LAB FURNISHING | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 1 | Y |  | CYT | Rm6007 | FH72 | FH072 | CHEM
FC020 | MAE | 6105 | LAB FURNISHING | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 1 | Y |  | EC | Rm6145 | FH319* | FH319 | CCM
FC026 | AEMF | 4229 | LAB FURNISHING | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220 |  |  |  | EC | Rm7161C | FH307c* | FH307c | CHEM
FC028 | CBE | 7101 | LAB FURNISHING | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FC029 | HSEO | 3107 | WALDNER | 1500 | EF-K-157-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 239 | 1 | N (Wait for Budget)
FC030 | HSEO | 3107 | WALDNER | 1500 | EF-K-157-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 239 | 1 | N (Wait for Budget)
FC031 | ECE | 2227 | LAB FURNISHING | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
FC032 | CHEM | 6120 | LAB FURNISHING | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FC037 | LIFS | 6319 | LAB FURNISHING | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
FC038 | CBE | 7104 | CLEAN AIR | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FC040 | ECE | 3112 | LAB FURNISHING | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FC041 | CHEM | 2123 | LAB FURNISHING | 1500 | EF-K-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FC042 | ECE | 2166 | LAB FURNISHING | 1500 | EF-L3-157-107/108 | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
FC048 | CHEM | 7133 | LAB FURNISHING | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FC049 | AEMF | 4229 | LAB FURNISHING | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
FC053 | CHEM/LIFS | 2229 | LAB FURNISHING | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FC054 | ECE | 2166 | LAB FURNISHING | 1200 | EF-L3-157-107/108 | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FC055 | LIFS | 6306 | LAB FURNISHING | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FC056 | LIFS | 6256A | LAB FURNISHING | 1200 |  | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH005 | PHYS | 4118 | MORGAN & GRUNDY | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH006 | PHYS | 4121B | MORGAN & GRUNDY | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH007 | PHYS | 4123 | MORGAN & GRUNDY | 1200 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 1 | Y
FH008 | PHYS | 4126 | MORGAN & GRUNDY | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH010 | PHYS | 4139 | LAB FURNISHING | 1200 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 1 | Y
FH011 | PHYS | 4141 | MORGAN & GRUNDY | 1200 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 1 | Y
FH017 | CHEM | 6120 | LAB FURNISHING | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH018 | CHEM | 6122 | LAB FURNISHING | 1800 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 374 | 1 | Y
FH020 | CHEM | 6122 | KOTTRERMAN | 1500 | EF-L-157-102A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 1 | Y
FH021 | CHEM | 6122 | KOTTRERMAN | 1500 | EF-L-157-102A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 1 | Y
FH022 | CHEM | 6125 | KOTTERMAN | 1800 | EF-L-157-102A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325 | 1 | Y
FH023 | CHEM | 7122A | KOTTERMAN | 1800 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325
FH024 | CHEM | 6125 | KOTTERMAN | 1800 | EF-L-157-102A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325 | 1 | Y
FH025 | CBE | 6114 | KOTTERMAN | 1800 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325
FH026 | CHEM | 6124B | WALDNER | 1800 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 81 | 100mm | 212
FH028 | PHYS | 6138 | MORGAN & GRUNDY | 1200 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 1 | Y
FH031 | CBE | 7111 | MORGAN & GRUNDY | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH032 | CBE | 7111 | MORGAN & GRUNDY | 1500 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH033 | CHEM | 7133 | MORGAN & GRUNDY | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH039 | CHEM | 6124B | WALDNER | 1800 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 81 | 100mm | 212
FH040 | CHEM | 6125 | KOTTERMAN | 1800 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325
FH041 | CHEM | 6122 | KOTTRERMAN | 1800 | EF-L-157-102A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 325 | 1 | Y
FH042 | CHEM | 7121 | MORGAN & GRUNDY | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH043 | LIFS | 6313 | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH044 | CHEM | 7130 | MORGAN & GRUNDY | 1200 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 1 | Y
FH045 | CHEM | 7133 | MORGAN & GRUNDY | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH046 | CHEM | 7132 | WALDNER | 1500 | EF-L-157-102A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 239 | 1 | N (Wait for Budget)
FH048 | CHEM | 7134 | MORGAN & GRUNDY | 1200 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 1 | Y
FH049 | CHEM | 7136 | MORGAN & GRUNDY | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH050 | CBE | 7104 | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270
FH051 | CBE | 6113 | KOTTERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 1 | Y
FH053 | CHEM | 7139 | KOTTRERMAN | 1500 | EF-L-157-103A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 1 | Y
FH054 | CHEM | 7139 | KOTTRERMAN | 1500 | EF-L-157-103A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 1 | Y
FH055 | AEMF | 4228 | KEWAUNE | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 327
FH059 | CBE | 6118 | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 1 | Y
FH061 | CBE | 6121 | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 1 | Y
FH062 | CHEM | 7139 | KOTTRERMAN | 1500 | EF-L-157-103A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270
FH063 | CHEM | 6014A | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH064 | CHEM | 6014 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH065 | CHEM | 6007 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH066 | CHEM | 6007 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH067 | ENVF | 4109C | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270
FH068 | CHEM | 6014 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH069 | ENVF | 4109C | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270
FH070 | CHEM | 6014 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH072 | CHEM | 6007 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH075 | AEMF | 4229 | MORGAN & GRUNDY | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
FH076 | ENVR | 4096 | WALDNER | 1500 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171
FH078 | CBE | 6119 | KOTTRERMAN | 1500 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 1 | Y
FH079 | CHEM | 7130 | MORGAN & GRUNDY | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH083 | CBE | 7102 | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270
FH084 | CBE | 6114 | KOTTRERMAN | 1500 | EF-K-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 1 | Y
FH085 | CBE | 7112 | KOTTRERMAN | 1500 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 1 | Y
FH086 | LIFS | 6294 | MORGAN & GRUNDY | 1500 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
FH091 | CBE | 7112 | KOTTRERMAN | 1500 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 270 | 1 | Y
FH092 | LIFS | 6318 | KOTTERMAN | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 270
FH097 | LIFS | 6277 | LAB FURNISHING | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH099 | LIFS | 6274 | LAB FURNISHING | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH100 | CHEM | 7122A | MORGAN & GRUNDY | 2100 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 95 | 100mm | 446 | 1 | Y
FH102 | LIFS | 6314A | LAB FURNISHING | 2400 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 108 | 100mm | 522
FH103 | LIFS | 6278 | MORGAN & GRUNDY | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH104 | LIFS | 6279 | MORGAN & GRUNDY | 1200 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH106 | LIFS | 6286 | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH107 | LIFS | 6287 | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH108 | LIFS | 6288 | MORGAN & GRUNDY | 1500 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
FH110 | LIFS | 6293 | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH113 | LIFS | 6295B | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH114 | LIFS | 6296 | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH115 | LIFS | 6311 | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH119 | CLS | 1215 | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH129 | LIFS | 6248 | LAB FURNISHING | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH130 | LIFS | 6246 | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH132 | LIFS | 6244 | LAB FURNISHING | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH134 | LIFS | 6312 | MORGAN & GRUNDY | 1200 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH135 | LIFS | 6237 | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH136 | LIFS | 6243 | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH137 | LIFS | 6233B | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH138 | LIFS | 6225 | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH140 | LIFS | 6231 | MORGAN & GRUNDY | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH142 | LIFS | 6224 | MORGAN & GRUNDY | 1200 | EF-J-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH143 | LIFS | 6223 | MORGAN & GRUNDY | 1200 | EF-J-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH144 | LIFS | 6220 | MORGAN & GRUNDY | 1200 | EF-J-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH145 | LIFS | 6219 | MORGAN & GRUNDY | 1200 | EF-J-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH161 | ECE | 1047A | MORGAN & GRUNDY | 1500 | EF-ENT-140-4 | BBQ | Y | N |  | N | N | N | N/A | N/A | N/A | N/A
FH162 | ECE | 1047A | MORGAN & GRUNDY | 1500 | EF-ENT-140-4 | BBQ | Y | N |  | N | N | N | N/A | N/A | N/A | N/A
FH163 | ECE | 1047A | MORGAN & GRUNDY | 1500 | EF-ENT-140-4 | BBQ | Y | N |  | N | N | N | N/A | N/A | N/A | N/A
FH166 | LIFS | 6221 | MORGAN & GRUNDY | 1200 | EF-J-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 220
FH167 | ECE | 1043 | MORGAN & GRUNDY | 1200 | EF-ENT-140-4 | BBQ | Y | N |  | N | N | N | N/A | N/A | N/A | N/A
FH169 | AEMF | 4229 | MORGAN & GRUNDY | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
FH170 | ECE | 1047A | MORGAN & GRUNDY | 1200 | EF-ENT-140-4 | BBQ | Y | N |  | N | N | N | N/A | N/A | N/A | N/A
FH177 | CBE | 7102 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH178 | MCPF | 2151 | MORGAN & GRUNDY | 1500 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH181 | PHYS | 4119B | LAB FURNISHING | 1200 | EF-L-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 220 | 1 | Y
FH182 | MAE | G031A | MORGAN & GRUNDY | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH191 | BRI | 6141 | MOTT | 1800 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 396 | 1 | Y
FH192 | BRI | 7152 | MOTT | 1800 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 394 | 1 | Y
FH195 | CHEM | 7137 | MOTT | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH206 | PHYS | 4145 | NUAIRE | 1800 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 264 | 1 | Y
FH209 | BCRF | 6127 | CMS | 1200 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 245 | 1 | Y
FH226 | CIVL | 1211 | LAB FURNISHING | 1500 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 297
FH227 | LIFS | CML | CHEMFAST | 1200 |  | DUCTLESS |  |  |  | Y | N | N | 0.35M/S at 200mm sash height | N/A | N/A | N/A
FH230 | CBE | 6104 | APMG | 1200 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 235 | 1 | Y
FH231 | PHYS | 4145 | APMG | 1200 | EF-L-157-103A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 235 | 1 | Y
FH232 | CBE | 7250 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH233 | CBE | 7250 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH234 | CBE | 7252 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH235 | CBE | 7252 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH236 | CBE | 7253 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH237 | CBE | 7253 | MOTT | 1500 | EF-J-152-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH240 | CHEM | 6007 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH243 | MAE | 4225 | KEWAUNE | 1500 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 327
FH245 | ECE | 3125B | ESCO | 1200 |  | DUCTLESS |  |  |  | Y | N | N | 0.35M/S at 200mm sash height | N/A | N/A | N/A
FH247 | CBE | 7103 | KEWAUNE | 1800 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 403 | 1 | Y
FH248 | CBE | 7103 | KEWAUNE | 1800 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 81 | 100mm | 403 | 1 | Y
FH251 | ENVR | 4114 | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH252 | MAE | 4225 | MOTT | 1500 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319
FH253 | ECE | 2234 | MOTT | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319
FH254 | MAE | 4222 | MOTT | 1500 | EF-H-152-102A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319
FH255 | CHEM | 7135 | MOTT | 1500 | EF-L-157-102A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH256 | CBE | 7107 | WALDNER | 1500 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH257 | CBE | 7108 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH258 | CBE | 7108 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH259 | CBE | 7109 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH260 | CBE | 7109 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH261 | CBE | 7110 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH262 | CBE | 7118 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH263 | CHEM | 7122 | LABCONKO | 1800 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 304
FH264 | CHEM | 7122 | THERMO- FISHER | 1800 | EF-L-157-101A | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 81 | 100mm | 308
FH265 | MAE | 1213 | KEWAUNE | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 228
FH266 | MAE | 4222B | WALDNER | 1500 | EF-H-152-06 | BBQ | Y | N | Y | N | N | N | N/A | N/A | N/A | N/A
FH267 | LIFS | 6255 | MOTT | 1200 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 55 | 100mm | 245
FH268 | LIFS | CML | CHEMFAST | 1500 |  | DUCTLESS |  |  |  | Y | N | N | 0.35M/S at 200mm sash height | N/A | N/A | N/A
FH269 | CBE | 6115 | WALDNER | 1500 | EF-K-157-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 239 | 1 | N (Wait for Budget)
FH270 | CBE | 6115 | WALDNER | 1500 | EF-K-157-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 239 | 1 | N (Wait for Budget)
FH271 | CIVL | 3212 | WALDNER | 1500 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH272 | CHEM | 7132 | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH273 | BRI | 4150 | WALDNER | 1500 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH274 | BRI | 4150 | WALDNER | 1500 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH275 | CHEM | 7166 | WALDNER | 1500 | EF-L3-157-107/108 | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH276 | CHEM | 7166 | WALDNER | 1500 | EF-L3-157-107/108 | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH277 | PHYS | 4115 | WALDNER | 1200 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 1 | N (Wait for Budget)
FH278 | PHYS | 4115A | WALDNER | 1200 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 1 | N (Wait for Budget)
FH279 | PHYS | 4116A | WALDNER | 1200 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 1 | N (Wait for Budget)
FH280 | PHYS | 4117 | WALDNER | 1200 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 1 | N (Wait for Budget)
FH281 | PHYS | 4115D | RENGGLI | 1200 | EF-K-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160
FH282 | PHYS | 4116B | RENGGLI | 1200 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160
FH283 | LIFS | 4218 | CHEMFAST | 1500 |  | DUCTLESS |  |  |  | Y | N | N | 0.35M/S at 200mm sash height | N/A | N/A | N/A
FH285 | CBE | 6117 | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH286 | PHYS | 4125 | RENGGLI | 1200 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160
FH287 | PHYS | 4125 | RENGGLI | 1200 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160
FH288 | CHEM | 6124B | RENGGLI | 1200 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160
FH289 | CHEM | 6124B | RENGGLI | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 201
FH290 | LIFS | 2230K | WALDNER | 1200 | EF-H-152-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160
FH291 | CIVL | 1207C | RENGGLI | 1500 | EF-J-152-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 201
FH292 | PHYS | 4142 | RENGGLI | 1500 | EF-L-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 55 | 100mm | 201
FH293 | LIFS | 6320 | WALDNER | 1500 | EF-H-152-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 239
FH294 | CIVL | 1209C | WALDNER | 1500 | EF-J-152-101A | LOW | N | Y | Y | N | Y | N | 0.3 - 0.4m/s | 55 | 100mm | 239
FH301 | ENVR | 4113 | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH302 | CBE | 7107 | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH303 | IAS | 7164 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH304 | CHEM | 7162 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH305 | CHEM | 7162 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH306 | CHEM | 7161C | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH307 | CHEM | 7161C | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH308 | CHEM | 7161A | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH309 | CHEM | 7161A | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH310 | MNF | 7163 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH311 | MNF | 7163 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH312 | LIFS | 6260 | MOTT | 1500 | EF-J-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319
FH313 | IAS | 7165 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH314 | LIFS | 7167 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH315 | MAE | G031A | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319
FH317 | R&D | 6147 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH318 | CLS | 6109 | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319
FH319 | CCM | 6145 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH320 | CCM | 6145 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH321 | CHEM | 6143 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH322 | CHEM | 6143 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH323 | NAMI | 6150 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH324 | CAMP | 2162A | MOTT | 1500 | EF-L3-157-107/108 | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319
FH325 | BCRF | 6146 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH326 | CBE | 7107 | MOTT | 1500 | EF-K-157-101A | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH327 | FINTEX | 6148 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH328 | FINTEX | 6148 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH330 | MAE | 4227 | MOTT | 1500 | EF-H-152-101A | CAV | Y | N |  | Y | N | N | 0.45M/S at 500mm sash height | 67 | 100mm | 319
FH331 | LIFS | 4160B | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH332 | LIFS | 4160 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH333 | LIFS | 4160 | MOTT | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 319 | 1 | Y
FH401 | CHEM | UG002 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH402 | CHEM | UG002 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH403 | CHEM | UG002 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH404 | CHEM | UG001 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH405 | CHEM | UG001 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH406 | CHEM | UG001 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH407 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH408 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH409 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH410 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH411 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH412 | CHEM | UG001 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH413 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH414 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH415 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH416 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH417 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH418 | CHEM | UG001 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH419 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | N (wait for Parts)
FH420 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH421 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH422 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH423 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH424 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH425 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH426 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH427 | CHEM | 1003 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH428 | CHEM | 1004 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH429 | CHEM | 1004 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH430 | CHEM | 1004 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH431 | CHEM | 1004 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH432 | CHEM | 1004 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH433 | CHEM | 1004 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH434 | CHEM | 7166 | CLEAN AIR | 1500 | EF-L3-157-107/108 | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH435 | CHEM | 7166 | CLEAN AIR | 1500 | EF-L3-157-107/108 | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH436 | CHEM | 7166 | CLEAN AIR | 1500 | EF-L3-157-107/108 | LOW | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH437 | CHEM | UG001 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH438 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Yes
FH439 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Yes
FH440 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Yes
FH441 | CHEM | 1004 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH442 | CHEM | 1004 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Y
FH443 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | Low | N | Y |  | N | Y | N | 0.3 - 0.4m/s | 67 | 100mm | 198 | 1 | Yes
FH444 | CBME | 2007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH445 | CBME | 2007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH446 | CBME | 2007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH447 | CBME | 2007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH448 | CBME | 2007B | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH449 | CBME | 2007B | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH450 | ECE | 4014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH451 | ECE | 4014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH452 | BME | 3007E | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH453 | CBME | 2007A | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH454 | ECE | 3014D | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH455 | ECE | 3014C | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH456 | EI | 4007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH457 | EI | 4007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH458 | EI | 4007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH459 | EI | 4007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH460 | EI | 4007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH461 | MAE | 4007C | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH462 | MAE | 4007C | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH463 | ECE | 4014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH464 | ECE | 4014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH465 | ECE | 4014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH466 | ECE | 4014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH467 | ECE | 4014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH468 | ECE | 4014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH469 | ECE | 4014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH470 | LIFS | 5007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH471 | LIFS | 5007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH472 | LIFS | 5007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH473 | LIFS | 5014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH474 | LIFS | 5014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH475 | ECE | 2164 | CLEAN AIR | 1500 | EF-L3-157-107/108 | VNOR | N | Y |  | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH476 | MAE | 4225 | CLEAN AIR | 1500 | EF-H-152-102A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH477 | LIFS | 5014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH478 | LIFS | 5014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH479 | LIFS | 5014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH480 | LIFS | 5014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH481 | LIFS | 5014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH482 | LIFS | 5014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH483 | LIFS | 5014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH484 | LIFS | 5014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH485 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH486 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH487 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH488 | ENVR | 4094 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH489 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH490 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH491 | ENVR | 4105 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH493 | MAE | 4225 | CLEAN AIR | 1500 | EF-H-152-102A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH494 | ENVR | 4094 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH495 | ENVR | 4111 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH496 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH497 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH498 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH499 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH500 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH501 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH502 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH503 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH504 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH505 | SENG | 1002 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH506 | CBE | 7106 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297 | 1 | Y
FH507 | CHEM | 6007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH508 | CHEM | 6007A | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH510 | EI | 4007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH511 | EI | 4007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH512 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH513 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH514 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH515 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH516 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH517 | ENVR | 4094 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH518 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH519 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH520 | ENVR | 4094 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH521 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH522 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH523 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH524 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH525 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH526 | EI | 4007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH527 | ENVR | 4110 | CLEAN AIR | 1500 | EF-K-157-101A | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH528 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH529 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH530 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH531 | CHEM | 6014 | CleanAir | 1500 | SEAF-L4-172-8,9,10 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH532 | EI | 4007 | CleanAir | 1500 | SEAF-L4-172-5,6,7 | VNOR | N | Y | Y | Y | N | N | 0.4 - 0.5m/s | 67 | 100mm | 297
FH600 | ECE | 4014 | Waldner | 1800 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 81 | 100mm | 212
FH601 | CHEM | 6007 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH602 | CHEM | 6007 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH603 | CHEM | 6007 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH604 | CHEM | 6007 | Waldner | 1500 | SEAF-L4-172-5,6,7 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH605 | CHEM | 6014 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH606 | CHEM | 6014 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH607 | CHEM | 6014 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH608 | CHEM | 6014 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH609 | CHEM | 6014 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH610 | CHEM | 6014 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH611 | CHEM | 6014 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH612 | CHEM | 6014 | Waldner | 1500 | SEAF-L4-172-8,9,10 | EXTLow | N | Y | Y | N | N | Y | 0.2 -0.3m/s | 55 | 100mm | 171 | 1 | N (Will do)
FH700 | CHEM | 6125 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH701 | CHEM | 6125 | WALDNER | 1500 | EF-L-157-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH702 | CHEM | 6125 | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH703 | CHEM | 6125 | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH704 | CIVL | 3202 | WALDNER | 1500 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH705 | CIVL | 3201 | WALDNER | 1500 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH706 | CIVL | 3201 | WALDNER | 1500 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH707 | CIVL | 3201 | RENGGLI | 1500 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 201
FH708 | NAMI | 6149 | RENGGLI | 1200 | EF-L3-157-107/108 | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 1 | Y
FH709 | NAMI | 6149 | RENGGLI | 1200 | EF-L3-157-107/108 | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 1 | Y
FH710 | CHEM | 2228 | CHEMFAST | 1200 |  | DUCTLESS |  |  |  | Y | N | N | 0.35M/S at 200mm sash height | N/A | N/A | N/A
FH711 | LIFS | 6201 | WALDNER | 1200 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 1 | N (Wait for Budget)
FH712 | LIFS | 6201 | WALDNER | 1200 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 1 | N (Wait for Budget)
FH713 | LIFS | 6201 | WALDNER | 1200 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 1 | N (Wait for Budget)
FH714 | LIFS | 6201 | WALDNER | 1200 | EF-J-152-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 1 | N (Wait for Budget)
FH719 | CHEM | 7153 | WALDNER | 1200 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 160 | 1 | N (Wait for Budget)
FH720 | CHEM | 7153 | WALDNER | 1500 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH721 | CHEM | 7153 | WALDNER | 1500 | EF-L-157-103A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH722 | CHEM | 7132 | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH723 | CHEM | 7132 | WALDNER | 1500 | EF-L-157-102A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171 | 1 | N (Wait for Budget)
FH724 | PHYS | 2237 | WALDNER | 1500 | EF-H-152-101A | EXTLow | N | Y | Y | N | N | Y | 0.2 - 0.3m/s | 55 | 100mm | 171
196